Frequency: Annual Action Electric Fire Pump

Pump System

Yes No N/A Inspect/Change

(as needed) Lubricate bearings

Yes No N/A Test Power transfer switch

Yes No N/A Inspect Check parallel and angular alignment

Yes No N/A Test Main relief valve

Yes No N/A Inspect Check flexible hoses and connections

Yes No N/A Inspect Check plumbing parts — inside and outside panels

Yes No N/A Inspect Check pump shaft end play

Yes No N/A Inspect/Change Check accuracy of pressure gauges and sensors

Yes No N/A Inspect Pump coupling alignment

Mechanical Transmission

Yes No N/A Change Lubricate coupling (Alternative ITM A.8.1.1.2)

Yes No N/A Change Lubricate right angle gear drive (Alternative ITM A.8.1.1.2)

Electrical System

Yes No N/A Inspect Corrosion on printed circuit boards

Yes No N/A Inspect Cracked cable/wire insulation

Yes No N/A Test Electronic control module (ECM)

Yes No N/A Maintenance Sacrificial anode

Yes No N/A Test Trip circuit breaker (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect/Test Operate emergency manual starting means (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect Lubricate mechanical moving parts (except starters and relays)

(Alternative ITM A.8.1.1.2)

Yes No N/A Inspect Calibrate pressure switch settings (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect Lubricate motor bearings (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect Leaks in plumbing parts (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect Signs of water on electrical parts (Alternative ITM A.8.1.1.2)

Frequency: Annual Diesel Engine System

Pump System

Yes No N/A Test Main relief valve

Fuel

Yes No N/A Test Diesel fuel

Yes No N/A Test Fuel pump alarm signals

Yes No N/A Maintenance Active fuel maintenance system

Yes No N/A Clean Change fuel filter every 50 operating hours or annually

Yes No N/A Clean Water/foreign material in tank (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect/Test Tank vents and overflow piping unobstructed

Yes No N/A Inspect Fuel tank piping (Alternative ITM A.8.1.1.2)

Lubrication System

Yes No N/A Change Oil change (50 hour maximum)

Yes No N/A Change Oil filter(s) (50 hour maximum)

Cooling System

Yes No N/A Maintenance Replace circulating water filter

Yes No N/A Test Supervisory signal for high cooling water temperature

Yes No N/A Inspect Antifreeze (Alternative ITM A.8.1.1.2)

Yes No N/A Clean Heat exchanger (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect/Change Duct work/louvers (Alternative ITM A.8.1.1.2)

Exhaust System

Yes No N/A Inspect Check exhaust system and drain condensate trap

Yes No N/A Test Check for excessive backpressure

Yes No N/A Inspect Hangers and support in good condition (Alternative ITM A.8.1.1.2)

Battery System

Yes No N/A Maintenance Check specific gravity, state of charge, and charger rates

Yes No N/A Maintenance Clean terminals

Yes No N/A Maintenance

Check battery cranking voltage exceeds 9 volts for a 12 volt

system and 18 volts for a 24 volt system

Yes No N/A Maintenance Ensure only distilled water is used

Frequency: Annual Electrical System

Yes No N/A Inspect Corrosion on printed circuit boards

Yes No N/A Test Electrical control module (ECM)

Yes No N/A Inspect Tighten control and power wiring connectors (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect Voltmeter and ammeter for accuracy (5%) (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect Cracked cable/wire insulation (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect Leaks in plumbing parts (Alternative ITM A.8.1.1.2)

Yes No N/A Inspect Signs of water on electrical parts (Alternative ITM A.8.1.1.2)