Inspections: Daily (Cold Weather/Heating Season Only)

Yes No N/A Heating system (when not supervised)

Inspectons: Weekly Control Valves

Yes No N/A In the correct (open or closed) position

Yes No N/A Sealed

Yes No N/A Accessible

Yes No N/A Post Indicator Valves (PIVs) are provided with correct wrenches

Yes No N/A Free from damage or leaks

Yes No N/A Proper signage

(Cold Weather/Heating Season Only)

Yes No N/A Record Water temperature (when not supervised)

Yes No N/A Record water temperature (supervised systems)

Inspections: Monthly

Yes No N/A Gauges are in good operating condition

Control Valves (Locked or Supervised)

Yes No N/A Water temperature (supervised systems)

Yes No N/A In the correct (open or closed) position

Yes No N/A Locked or supervised

Yes No N/A Accessible

Yes No N/A Post Indicator Valves (PIVs) are provided with correct wrenches

Yes No N/A Free from damage or leaks

Yes No N/A Proper signage

Water Level

Yes No N/A Water level (unsupervised) full

Inspections: Quarterly

Yes No N/A Gauges — normal water pressure maintained

Yes No N/A Water level (supervised) full

Inspections: Quarterly Tank Exterior Inspection

Yes No N/A Exterior of tank, supporting structure, vents, foundation, and catwalks or ladders

are in good condition

Yes No N/A Area is free of combustible storage, trash, debris, brush, or material that could

present a fire exposure hazard

Yes No N/A Area is free of accumulation of material on or near parts that could result in

accelerated corrosion or rot

Yes No N/A Tank and support are free of ice buildup

Yes No N/A Exterior sides and top of embankments supporting coated fabric tanks are free of

erosion

(Cold Weather/Heating Season Only)

Yes No N/A Heating system (supervised systems)

Control Valves (Electronically Supervised)

Yes No N/A In the correct (open or closed) position

Yes No N/A Electronically supervised

Yes No N/A Accessible

Yes No N/A Post Indicator Valves (PIVs) are provided with correct wrenches

Yes No N/A Free from damage or leaks

Yes No N/A Proper signage

Surrounding Area

Yes No N/A Free of combustibles

Yes No N/A Free of material that could accelerate corrosion or not

Yes No N/A Free of ice buildup

Yes No N/A Embankments (for coated fabric tank) free of erosion

Inspections: Annual

Yes No N/A Hoops and grillage (wooden tanks) are in good condition

Yes No N/A Painted/coated surfaces are in good condition

Yes No N/A Expansion joints are not cracked or leaking

Inspections: Three Years Steel Tank Interior Inspection (Without Corrosion Protection)

Yes No N/A Silt has been removed for underwater evaluation

Yes No N/A Interior surfaces are free of pitting, corrosion, spalling, or other forms of deterioration

Yes No N/A Interior is free of waste material, aquatic growth, and debris

Yes No N/A Interior coating is intact

Yes No N/A Tank floor is free of dents

Yes No N/A Heating system and components are in good condition

Yes No N/A Anti-vortex plate is in good condition and is not obstructed

Inspections: Five Years Interior Inspection (All Other Tank Types)

Yes No N/A Silt has been removed for underwater evaluation

Yes No N/A Interior surfaces are free of pitting, corrosion, spalling, or other forms of deterioration

Yes No N/A Interior is free of waste material, aquatic growth, and debris

Yes No N/A Interior coating is intact

Yes No N/A Tank floor is free of dents

Yes No N/A Heating system and components are in good condition

Yes No N/A Anti-vortex plate is in good condition and is not obstructed

Check Valves

Yes No N/A Check valve — internal moves freely and in good condition

Test Prior to Heating Season Tank Heating System

Yes No N/A In proper working order

Yes No N/A Low water temperature signals

Yes No N/A High water temperature signals

Test: Monthly Water Temperature

Yes No N/A Low temperature alarm is working correctly

Yes No N/A High temperature limit switch is working correctly

Test: Semiannual

Yes No N/A High and low water level signals work correctly

Test: Annual Valve Status

Yes No N/A Operated through its full range of motion

Yes No N/A Status test to verify valve(s) is in the open position

Automatic Tank Fill Valve

Yes No N/A Valve actuated by lowering water level

Yes No N/A Measure and record refill rate

Test: Five Years

Yes No N/A Level indicators are accurate and move freely

Yes No N/A Gauges tested or replaced

Maintenance

Yes No N/A Tank maintained full or at designated water level

Yes No N/A Hatch covers in the roofs and the door at the top of frost-proof castings kept

securely fastened

Yes No N/A Waste material in or on the tank

Yes No N/A Clean strainers quarterly