Inspections: Weekly Pump House

Yes No N/A Heat in pump room is 40°F (4°C) or higher

Yes No N/A Ventilation louvers are free to operate

Yes No N/A Excessive water does not appear on the floor

Yes No N/A Coupling guard is in place

Yes No N/A Heat in pump room is not less than 70°F (21°C) for diesel engine pump without

engine heater

Pump Systems

Yes No N/A Pump suction, discharge, and bypass valves are open

Yes No N/A No piping or hoses leak

Yes No N/A Fire pump leaking one drop of water per second at seals

Yes No N/A Suction line pressure is within acceptable range

Yes No N/A System line pressure is within acceptable range

Yes No N/A Suction reservoir is full

Yes No N/A Wet pit suction screens are unobstructed and in place

Yes No N/A Waterflow test valves are in closed position, hose connection valve is closed, and the

line to test valves is free of water

Electrical Systems

Yes No N/A Controller pilot light (power on) is illuminated

Yes No N/A Transfer switch normal power light is illuminated

Yes No N/A Isolating switch for standby power is closed

Yes No N/A Reverse-phase alarm light is not illuminated

Yes No N/A Normal-phase rotation light is illuminated

Yes No N/A Oil level in vertical motor sight glass is within acceptable range

Yes No N/A Pressure maintenance (jockey) pump has power

Diesel Engine Systems

Yes No N/A Diesel fuel tank is at least two-thirds full

Yes No N/A Controller selector switch is in “auto” position

Yes No N/A Voltage readings for batteries (2) are within acceptable range

Yes No N/A Charging current readings are within acceptable range for batteries

Yes No N/A Pilot lights for batteries are “on” or battery failure

pilot lights are “off”

Inspections: Weekly

Yes No N/A All alarm pilot lights are “off”

Yes No N/A Record engine running time from meter

Yes No N/A Oil level is within acceptable range in right angle gear drive pumps

Yes No N/A Crankcase oil level is within acceptable range

Yes No N/A Cooling water level is within acceptable range

Yes No N/A Electrolyte level in batteries is within acceptable range

Yes No N/A Battery terminals are free of corrosion

Yes No N/A Water-jacket heater is operational

Yes No N/A Battery cranking voltage exceeds 9 volts for a 12 volt system and 18 volts for a 24 volt

system (Alternative ITM A.8.1.1.2)

Yes No N/A Water pump(s) is not leaking (Alternative ITM A.8.1.1.2)

Yes No N/A Jacket water heater operational (Alternative ITM A.8.1.1.2)

Yes No N/A Flexible hose and connections are in good operating condition (Alternative

ITM A.8.1.1.2)

Yes No N/A Check lube oil heater for operation (Alternative ITM A.8.1.1.2)

Yes No N/A Oil lube level is within acceptable range (Alternative ITM A.8.1.1.2)

Yes No N/A Check for water in diesel fuel tank (Alternative ITM A.8.1.1.2)

Steam System

Yes No N/A For steam-driven pumps, steam pressure is within acceptable range

Exhaust System

Yes No N/A Examine exhaust system for leaks (Alternative ITM A.8.1.1.2)

Yes No N/A Drain condensate trap (Alternative ITM A.8.1.1.2)

Inspections: Weekly

Pump Systems

Yes No N/A Record pump starting pressure psi

Yes No N/A Operate fire pump for 10 minutes (30 minutes for diesel pump)

Yes No N/A Check packing gland tightness (slight leak at no flow)

Yes No N/A Record suction pressure from gauge in psi

Yes No N/A Record discharge pressure from gauge in psi

Yes No N/A Adjust gland nuts if necessary

Yes No N/A Check for unusual noise or vibration

Yes No N/A Check packing boxes, bearings, or pump casing for overheating

Yes No N/A Record pressure switch or pressure transducer and compare with pump

discharge gauge

Yes No N/A Record pumps highest psi and lowest psi pressure

on the fire pump control log

Yes No N/A Circulation relief valve functions correctly

Yes No N/A Check fuel system solenoids for proper operation (Alternative

ITM A.8.1.1.2)

Yes No N/A Check tank float switch for proper operation (Alternative ITM A.8.1.1.2)

Electrical Systems

Yes No N/A Record time controller is on first step (for reduced voltage or reduced

current starting)

Yes No N/A Observe time for motor to accelerate to full speed

Yes No N/A Record time pump runs after starting for pumps having automatic stop

feature

Diesel Engine Systems

Yes No N/A Record time for diesel engine to crank

Yes No N/A Record time for diesel engine to reach running speed

Yes No N/A Check oil pressure gauge, speed indicator and water and oil temperatures

while engine is running

Yes No N/A Check heat exchanger for cooling water flow

Yes No N/A Operate speed governor (internal combustion engine only)

Steam System

Yes No N/A Observe the time for turbine to reach running speed

Yes No N/A Record steam pressure for steam-operated pumps

Yes No N/A Check steam trap

Yes No N/A Check steam relief valve