PRIVATE FIRE SERVICE MAINS INSPECTION, TESTING, AND MAINTENANCE

Inspections: Weekly Control Valves

Yes No N/A In the correct (open or closed) position

Yes No N/A Sealed

Yes No N/A Accessible

Yes No N/A Post Indicator Valves (PIVs) are provided with correct wrenches

Yes No N/A Free from damage or leaks

Yes No N/A Proper signage

Backflow

Yes No N/A Isolation valves are in open position and locked or supervised

Yes No N/A RPA and RPDA - differential-sensing relief valve operating correctly

Inspections: Monthly Control Valves (Locked or Supervised)

Yes No N/A In the correct (open or closed) position

Yes No N/A Locked or supervised

Yes No N/A Accessible

Yes No N/A Post Indicator Valves (PIVs) are provided with correct wrenches

Yes No N/A Free from damage or leaks

Yes No N/A Proper signage

Inspections: Quarterly Control Valves (Electronically Supervised)

Yes No N/A In the correct (open or closed) position

Yes No N/A Electronically supervised

Yes No N/A Accessible

Yes No N/A Post Indicator Valves (PIVs) are provided with correct wrenches

Yes No N/A Free from damage or leaks

Yes No N/A Proper signage

Fire Department Connections

Yes No N/A Visible and accessible

Yes No N/A Coupling/swivels operate correctly

Yes No N/A Plugs/caps are in place

Inspections: Quarterly Fire Department Connections

Yes No N/A Gaskets are not damaged

Yes No N/A Automatic drain valve in place and operating properly

Yes No N/A Identification signs are in place

Yes No N/A Interior is clear of obstructions (unless locked)

Yes No N/A Clapper(s) operates correctly

Yes No N/A Check valve not leaking

Yes No N/A Visible piping supplying the fire department connection is undamaged

Hose Houses

Yes No N/A Accessible

Yes No N/A Free from damage or leaks

Yes No N/A No missing equipment

Dry Hydrant

Yes No N/A Water supply is not deteriorated in pond, stream, or cistern.

Yes No N/A Vegetation cleared 3 ft (0.9 m) radius from hydrant

Inspections: Semiannual Monitor Nozzles

Yes No N/A Not leaking

Yes No N/A Free of damage

Yes No N/A Free of corrosion

Dry Hydrants

Yes No N/A Reflective material marking and signage is in accordance with 8.4.7 of NFPA 1142

Inspections: Annual Hydrants (Dry Barrel and Wall Type)

Yes No N/A Accessible

Yes No N/A Barrel is free of water and ice

Yes No N/A Barrel drains properly

Yes No N/A Not leaking

Yes No N/A Barrel is free of cracks

Yes No N/A Outlets are not excessively tight and lubricated

Yes No N/A Nozzle threads are not worn

Yes No N/A Operating nut is not worn

Yes No N/A Operating wrench is available

Yes No N/A Free of detrimental corrosion

Inspections: Annual Hydrants (Wet Barrel)

Yes No N/A Accessible

Yes No N/A Not leaking

Yes No N/A Barrel is free of cracks

Yes No N/A Outlets not excessively tight and lubricated

Yes No N/A Nozzle threads are not worn

Yes No N/A Operating nut is not worn

Yes No N/A Operating wrench is available

Fire Department Connections

Yes No N/A Interior of connection with locked plugs or caps is free of obstructions

Mainline Strainers

Yes No N/A Not plugged or fouled

Yes No N/A Free of corrosion

Yes No N/A No damaged parts

Pipe and Fittings (exposed)

Yes No N/A Not leaking

Yes No N/A Free of damage and corrosion

Yes No N/A Hangers intact and not damaged

Inspections: Five Years

Yes No N/A Backflow - internal inspection

Yes No N/A Check valve - internal moves freely and in good condition

Yes No N/A Backflow - forward flow test at minimum flow rate of the system demand

Test: Annual Monitor Nozzles

Yes No N/A Flow test until all foreign material has cleared (not less than one minute)

Yes No N/A Operated through full range of motion

Dry Hydrant

Yes No N/A Flow Test

Hydrants

Yes No N/A Flow test until all foreign material has cleared (not less than one minute)

Yes No N/A Barrel drains within 60 minutes

Hydrant Isolation Valve

Yes No N/A Operated through full range of motion

Yes No N/A Status test (verify valve is in the open position)

Test: Five Years Piping (Exposed and Underground)

Yes No N/A Flow test piping at rate anticipated during a fire

Yes No N/A Flow test results comparable to previous test

Fire Department Connections

Yes No N/A Piping from fire department connection to fire department connection check valve

hydrostatically tested at 150 psi (10 bar) for at least 2 hours

Maintenance: Annual Mainline Strainers

Yes No N/A Removed, inspected, and cleaned

Hydrants

Yes No N/A Lubricate stems, caps, plugs, and threads

Yes No N/A Accessible (no snow, ice, or other material)

Yes No N/A Protected from damage

Monitor Nozzles

Yes No N/A Lubricate per manufacturer’s recommendations